Single Line to Ground Fault Calculation

Fault location: Bus-0002

One-line diagram with the input data and per-unit impedances:

Positive, negative and zero sequence impedance diagrams for a fault at Bus-0002:

Positive:

Z1 is equal to the Utility positive sequence impedance.

Therefore:

Z1 = 33.3336

Zero:

Z0 is practically equal to the Transformer zero sequence impedance because the Utility impedance is huge.

Therefore:

Z0 = 4.3484

.

Negative:

Z2 is equal to the Utility negative sequence impedance.

Therefore:

Z2 = 33.3336

Interconnected sequence networks with ZF = 0:

One-line with the Thevenin Equivalent impedance at Bus-0002:

Equation to calculate the Single Line to Ground fault:

In our example ZF = 0, therefore:

Ia = 3 / (33.3336 + 33.3336 + 4.3484) = 0.0422 pu

The base current at Bus-0002 is equal to the following:

Ibase = 100MVA / (1.732 * 13800) = 4183.7 A

The Single Line to Ground fault at Bus-0002 will be equal to the following:

I = Ia * Ibase = 0.0422 * 4183.7 = 176.74 A

The following is the one-line diagram with the fault current displayed:

Now we will determine the single line to ground current going through the transformer due to a single line to ground fault at Bus-0002.

Determining the Transformer sequence currents: I1T, I2T and I0T

From the zero sequence diagram, I1T and I2T is equal to zero

Zero:

Positive:

Negative:

From symmetrical components we know that Ia = I1 + I2 + I0 = 3I1

From the calculation above:

I1 = 0.0422 / 3 = 0.01407 pu

IaT = I1T + I2T + I0T

IaT = 0 + 0 + I0T

Applying current division in the zero sequence diagram

I0T = I1 [Z0UC /( Z0UC + Z0T)]

Z0UC = Z0U + Z0C = (4.1345 + j 33.0759) + (0.0026 + j 0.0006) = (4.1371 + j 33.0765)

Z0T = (0.8623 + j 4.9251)

I0T = 0.01407 (0.8697 + j 0.0055) = 0.0122 pu

The base current at Bus-0002, is equal to the following:

Ibase = 100MVA / (1.732 * 13800) = 4183.7 A

IaT = I0T * Ibase = 0.0122 * 4183.7 = 51.2 A

If you have additional question, please feel free to contact SKM Systems Analysis, Inc. at the number listed below.